## 1.4-DSR-FHS
S. N. | PWD-BMC-SSR-NDR | SSR No. / P. No. | PARTICULARS | UNIT | A | A | A | A | A | B | B | B | B | B | C | C | C | C | C | D | D | D | D | D | COURTYARD | PUMPROOM | QTY | UNIT RATE (₹) | TOTAL AMOUNT (₹)
A
1 | PWD-CSR |  | Supplying and installing G.I. Pipe above ground of 'C' Class ERW of following sizes conforming to IS:1239, along with necessary fittings and M.S. angle iron supports, with one coat of red oxide primer and two coats of Post office fire red enamel paint, duly tested to 1.5 times of working pressure, in an approved manner. as per specification no. FF-PP Thickness will be consider 8 mm
1.1 | PWD-CSR | 13-6-8/PWD-22-23/Page No. 219 | 200 mm dia | Rmt | [20 empty] | 403 |  | 343 | 3572 | 1225196
1.2 | PWD-CSR | 13-6-7/PWD-22-23/Page No. 219 | 150 mm dia | Rmt | A: 15; B: 15; C: 12; D: 12 |  |  | 54 | 2409 | 130086
2 | PWD-CSR |  | Supplying and installing G.I. Pipe under ground of 'C' Class ERW of following sizes conforming to IS:1239, alongwith necessary fittings and M.S. angle iron supports, duly tested to 1.5 times of working pressure, in an approved manner. as per specification no. FF-PP
2.1 | PWD-CSR | 13-6-8/PWD-22-23/Page No. 219 | 200 mm dia | Rmt | [20 empty] | 99 |  | 99 | 3572 | 353628
2.2 | PWD-CSR | 13-6-7/PWD-22-23/Page No. 219 | 150 mm dia | Rmt | A: 66; A: 66; A: 66; B: 66; B: 66; B: 66; C: 66; C: 66; C: 66; D: 1` |  |  | 525 | 2409 | 1264725
2.3 | PWD-CSR | 13-6-5/PWD-22-23/Page No. 219 | 80 mm dia | Rmt | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 |  | 36 |  | 43 | 1116 | 47988
3 | PWD-CSR | 13-7-35/PWD-22-23/Page No. 222 | Supplying and installing gun metal Stainless Steel single outlet hydrant valve morris pattern, oblique type, conforming to IS:5290, ISI mark, with G.M. blanks cap and M.S. or G.I. chain in an approved manner. complete as per specification No. FF-VL/HV | Nos | 1 | 3 | 3 | 3 |  | 1 | 3 | 3 | 3 |  |  | 3 | 3 | 3 |  |  | 1 | 1 | 1 |  | 10 |  | 42 | 5799 | 243558
4 | PWD-CSR |  | Fire Brigade Inlet connection
4.1 | PWD-CSR | 13-8-10/PWD-22-23/Page No. 222 | Supplying and erecting fire brigade header of 150 mm dia, for supplying water in fire tank complete as per specification no. FF-FA/FBC | Nos | [20 empty] | 1 |  | 1 | 9479 | 9479
4.2 | PWD-CSR | 13-8-11/PWD-22-23/Page No. 223 | Supplying and erecting fire brigade header (Siamese connection) 4 way ,of 150 mm dia for supplying water to wet riser system complete as per specification no. FF-FFA/SMC | Nos | [20 empty] | 3 |  | 3 | 11588 | 34764
5 | PWD-CSR | 13-8-2/PWD-22-23/Page No. 222 | Supplying and installing wall mounting swinging Hose reel drum as per IS:884 fitted with 19 mm dia. 30m high pressure polypropylene (Polyhose) long fitted with necessary accessories complete as per specification No. FF-FFA/HV | Nos | 2 | 3 | 3 | 3 |  | 1 | 3 | 3 | 3 |  |  | 3 | 3 | 3 |  |  | 1 | 1 | 1 |  |  |  | 33 | 6921 | 228393
6 | PWD-CSR | 13-8-13/PWD-22-23/Page No. 223 | Supplying and erecting 20/25mm Ø G.M. air release cock, with necessary G.I. coupling to be fitted on top of Air vessel or on wet riser as per specification No. FF-FFA/ARV | Nos | [22 empty] | 2 | 840 | 1680
7 | PWD-CSR | 13-8-4/PWD-22-23/Page No. 222 | Supplying fire fighting R.R.L. Hose pipe, 63mm dia,15m in length, fitted with necessary accessories complete as per complete as per specification no. FF-FFA/RRL | Nos | 2 | 6 | 6 | 6 |  | 2 | 6 | 6 | 6 |  |  | 6 | 6 | 6 |  |  | 2 | 2 | 2 |  |  |  | 42 | 5229 | 219618
8 | PWD-CSR | 13-8-7/PWD-22-23/Page No. 222 | Supplying Stainless Steel branch Pipe 63 mm Ø fitted with 20 mm dia detachable hexagonal nozzle as per specifications No. FF-FFA/NZ | Nos | [20 empty] | 20 |  | 34 | 1926 | 65484 | bar: A to A; B to B; C to C; D to D
9 | PWD-CSR |  | Supplying & erecting of Brass orifice plate |  | 1 | 3 | 3 | 3 |  | 1 | 3 | 3 | 3 |  |  | 3 | 3 | 3 |  |  | 1 | 1 | 1 |  | 20 |  | 52 |  | 0
9.1 | PWD-CSR | 13-8-16/PWD-22-23/Page No. 223 | Supplying and erecting one no. Brass orifice plate having 6mm. thickness, 140 mm outer dia of140 mm at every single outlet hydrant valve as per specification No. FF-FFA/OP | Nos | [20 empty] | 20 |  | 34 | 1009 | 34306 | bar: A to A; B to B; C to C; D to D
9.2 | PWD-CSR | 13-8-17/PWD-22-23/Page No. 223 | Supplying and erecting one no. Brass orifice plate having 6mm thickness,160 mm outer dia at every double outlet hydrant valve as per specification No. FF-FFA/OP | RO | [23 empty] | 1022 | 0
10 | PWD-CSR |  | M.S./CRCA Cabinet for Housing
10.1 | PWD-CSR | 13-8-19/PWD-22-23/Page No. 223 | Supplying and erecting M.S./ CRCA cabinet for housing Fire Brigade/ SIEMESE connections (size 1250x 400 x 300 mm.) made from 16 SWG sheet and angle iron 25mm. x 25 mm. x 4 mm. having front doors with viewing glass (8" x 6") and locking arrangement with necessary fixing material such as rubber bidding etc. duly painted in post box red colour | Nos | [20 empty] | 20 |  | 5 | 8249 | 41245 | bar: A to A; B to B; C to C; D to D
10.2 | PWD-CSR | 13-8-20/PWD-22-23/Page No. 223 | Supplying and erecting M.S./ CRCA cabinet for housing Floor Hydrant valve, hose pipe, hose reel and branch pipe (size 1000 mm x 736mm x 736 mm.) made from 16 SWG sheet and angle iron 25 mm. x 25 mm. x 4 mm. having front doors with viewing glass (8"x6") and locking arrangement with necessary fixing material such as rubber bidding etc. duly painted in post box red colour | Nos | [22 empty] | 18 | 15886 | 285948
11 | PWD-CSR | 13-7-31/PWD-22-23/Page No. 221 | Supplying & installing gun metal gate valve of size 20 mm /25mm dia having threaded ends conforming to IS:778, ISI mark, alongwith G.I. threaded nipple. (drain valve).as per specification No. FF-VL/GV | R0 | [23 empty] | 913 | 0
12 | PWD-CSR | 13-8-9/PWD-22-23/Page No. 222 | Supplying & erecting Gun Metal Chrome plated Nozzle, 19mm Ø complete erected with 4 nos Jubily clips duly clamped with polyhose / rubber hose pipe. as per specification No. FF-FFA/NZ | Nos | A: 2; A: 3; A: 3; A: 3; B: 1; B: 3; B: 3; B: 3; C: 3; C: 3; C: 3 |  |  | 30 | 961 | 28830
13 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supplying and installing glycerine filled pressure gauge of 100 mm (4 inch) diameter, having range 0–14 kg/cm² (or 0–200 PSI), with stainless steel case and internals, bottom entry connection (3/8" or 1/2" BSP), and dual scale dial (kg/cm² and PSI) | Nos | [22 empty] | 5 | 4430 | 22150 | bar: A; B; C
14 | PWD-CSR | 13-8-15/PWD-22-23/Page No. 223 | Supplying and installing pressure switch with 12/15 mm dia isolation valve, G.I. nipple, elbow, etc complete as per specification no. FF-FFA/PS | Nos. | [21 empty] | 5 | 5 | 1763 | 8815
15 | PWD-CSR | 13-7-20/PWD-22-23/Page No. 221 | Supplying & Installing cast iron double flange butterfly valve of size 100 mm dia. confirming to IS 13095 having cast iron body, FG 220 Nitrite rubber replaceable seat with moulded 'O' ring, C.I. powder coated disc flow control complete & tested to 1.5 times of working pressure in an approved manner. as per specification No. FF-VL/BFV | Nos. | [22 empty] | 3 | 4121 | 12363 | bar: A; B; C
16 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supply & Fixing of Water cum Foam Monitor Detachable type having discharge capacity of 1750 LPM @ 7 Kg / cm2 pressure made of C.S. Seamless tube conf. to hot dip galvanized having Gunmetal swivel joints with SS 304 with double row of SS 304 Ball Bearings, Horizontal rotation 360 Deg and Vertical rotation +80 o TO –40o Deg, inlet : 80 NB; OD: 200; PCD:160, 4 Holes (19MM), Al Alloy Aqua Nozzel with Pickup Tube of 3 Meter length and Stainer. Nozzle will be jet -spray type having arrangement for Foam induction also so that the same can be used as Foam Monitor also using Foam induction tube. Horizontal reach of monitor will be at least 35/45 Mtrs at 30 Deg angle in still air. AS PER IS 8442.
16.1 | NDR |  | Water Monitor | RO | [23 empty] | 28910 | bar: A; B
16.2 | NDR |  | Foam Monitor | Nos | [22 empty] | 3 | 28910 | 86730
17 | PWD-CSR | 13-8-1/PWD-22-23/Page No.222 | Supplying & installing One piece moulded HDPE / Fibre water tank. for -ve suction only, having capacity 1000 ltrs. fitted with necessary accessories complete as per specification No. FF-FFA/PT | RO | [21 empty] | 1 | 0 | 9804 | 0
18 | PWD-CSR |  | Supplying and installing cast iron Ball Type foot valve
18.1 | PWD-CSR | 13-7-2/PWD-22-23/Page No.219 | Supplying and installing cast iron foot valve ball type / flap type of size 100 mm dia with strainer for negative suction as per specification No. FF-VL/FV | Nos | [22 empty] | 0 | 6667 | 0
18.2 | PWD-CSR | 13-7-4/PWD-22-23/Page No.219 | Supplying and installing cast iron foot valve ball type / flap type of size200 mm dia with strainer for negative suction as per specification No. FF-VL/FV | Nos | [22 empty] | 0 | 31110 | 0
19 | PWD-CSR | 13-8-12/PWD-22-23/Page No.223 | Supplying and installing Air Vessel of 300 mm Ø 1.5m in height M.S. tank installed inside pump house as per specification No. FF-FFA/ACT | Nos | [21 empty] | 2 | 2 | 12472 | 24944
20 | PWD-CSR | 13-7-5/PWD-22-23/Page No.220 | Supplying and erecting 75/80 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF VL/ELS | Nos | [21 empty] | 2 | 2 | 4373 | 8746
20.1 | PWD-CSR | 13-7-6/PWD-22-23/Page No.220 | Supplying and erecting 100 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, SS screen, end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | Nos | [21 empty] | 3 | 3 | 6349 | 19047
20.2 | PWD-CSR | 13-7-8/PWD-22-23/Page No.220 | Supplying and erecting 200 mm dia Cast Iron end line strainer of Y-type flanged end pattern, PN16 pressure rating, screen of SS end connection with Flanged / Screwed / Socket Weld / Butt Weld End etc with standard OAR (open area Ratio) for positive suction complete as per specification no. FF-VL/ELS | Nos | [22 empty] | 3 | 21035 | 63105
21 | BMC |  | Providing and laying of non pressure NP2 Class of following sizes RCC Hume pipes preferably in half cylindrical form confirming to IS 458-1988
21.1 | BMC | R3-ME-2-19-d | 300 mm dia | Mtr | [22 empty] | 0 | 727 | 0
21.2 | BMC | R3-ME-2-19-c | 225 mm dia | Mtr | [20 empty] | 48 |  | 0 | 518 | 0
22 | PWD-CSR |  | Supplying, Installing and Commissioning approved make Ball valve of following Sizes
22.1 | PWD-CSR | 13-7-32/PWD-22-23/Page No.221 | Supplying & installing gun metal gate valve of size 25mm dia as per specification No. FF-VL/GV | Nos | [22 empty] | 27 | 1202 | 32454
22.2 | PWD-CSR | 13-7-33/PWD-22-23/Page No.221 | Supplying & installing gun metal gate valve of size 50mm dia as per specification No. FF-VL/GV | Nos | [22 empty] | 27 | 1289 | 34803
23 |  |  | Road Breaking & Re-Surfacing
23.1 | PWD-CSR | 16-1-5/PWD-22-23/Page No.238 | Excavating hard Rock or bituminous road by chiselling for preparing pit for pole / stay/earth plate / for laying cable/ pipe & clearing the site by removing debris & making the site as required complete. | Cum | [22 empty] | 50 | 1081 | 54050
23.2 | NDR | NDR (Quatation - Siddhi Tech Solution) | Making good the same after the work is satisfactorily completed Providing 50mm thick semi grout bituminous road surface including supplying all materials, preparing the existing road surface, laying the required thickness of metal layer, heating and spraying bitumen, spreading chips, laying seal coat and compacting complete as directed by Engineer in charge. (By using Bulk Asphalt 60/70 grade) Spec. No. Rd.60 Page No.232. | Sqm | [22 empty] | 50 | 1750 | 87500
24 |  |  | Removing and Demolishing
24.1 | PWD-SSR | Sr.No.1557/46.19/BDW8/Page No.297/SSR-22-23 | Removing Shahabad or Tandur stones /Cement tiles/ Pever Block / Marble mosaic tiles from floor without bed concrete including stacking the materials as directed with all leads, lifts, complete. As directed by Engineer in charge. | RO /SQM | [22 empty] | 0 | 45 | 0
24.2 | PWD-SSR | Sr.No.1550/46.12/BDW8/Page No.296/SSR-2023 | Removing lime or lean cement concrete including stacking the spoils as directed with all leads, lifts, complete. As directed by Engineer in charge. | RO /Cum | [22 empty] | 0 | 558 | 0
25 | NDR |  | Disposing of dismantling material of reinforced cement concrete stone / brick masonry from work site to 50m beyond the building area. Disposing of the surplus excavated materials by mechanical transport to the lead upto 2 km over the initial lead of 50 m including loading, unloading, spreading, levelling etc., As directed by Engineer in charge. | RO / Cum | [22 empty] | 0 | 287 | 0
26 | NDR | NDR | Fabrication, supply and installation of MS support as required but not covered under specific items as per drawings, specifications and as instructed by E-I-C. Material shall conform to IS-2062. | KG | [22 empty] | 150 | 150 | 22500
27 | PWD-CSR | 16-3-5/PWD-22-23/Page No.239 | Providing Cement concrete foundation for pump in 1:2:4 with required size and length of foundation bolts and nuts as per design and drawing etc complete (cost with wooden box is included). Etc completed as Directed | Cum | [22 empty] | 6 | 5011 | 30066
28 | PWD-SSR | Sr.No.381/11.04/CD 3B/Page No.81/SSR22-23 | Providing and laying in situ cement concrete of 1:4:8 proportion with trap/ granite / quartzite/ gneiss metal in foundation including necessary form work, compacting and curing etc. complete. (with reversible drum rtype mixer with SCADA with Natural / VSI standard Artificial Sand) | Cum | [22 empty] | 6 | 5780 | 34680
29 | PWD-CSR | 13-6-10/PWD-CSR-22-23/Page No.219 | Providing coating of Bitumen Paint & 4mm thick Wrapping as per IS 10221 for underground 150 mm Ring Main of Fire Fighting System. | Mtr | [21 empty] | 102 | 10 | 345 | 3450
30 | PWD-CSR | 13-6-11/PWD-CSR-22-23/Page No.219 | Providing coating of Bitumen Paint & 4mm thick Wrapping as per IS 10221 for underground 200 mm Ring Main of Fire Fighting System. | Mtr | [22 empty] | 24 | 423 | 10152
31 | PWD-CSR | 13-6-9/PWD-CSR-22-23/Page No.219 | Providing coating of Bitumen Paint & 4mm thick Wrapping as per IS 10221 for underground 80/100 mm Ring of Fire Fighting System.. | Mtr | [22 empty] | 12 | 249 | 2988
32 | PWD-SSR | Sr.No.1384/42.13/BDV43/Page No.275/PWD-SSR-22-23 | Providing and constructing Brick Masonry Inspection Chamber 90cm x 45cm x 90cm including 1:4:8 cement concrete foundation 1:2:4 cement concrete channels half round G.S.W. pipes, Brick Masonry, plastering from inside and with frame fixed in cement concrete with R.C.C. Cover medium duty 140 kg with frame etc complete. | RO /Nos | [22 empty] | 0 | 10777 | 0
33 | NDR | NDR | Supplying and fixing of Expansion Bellow Valve Neoprene Rubber Expansion Bellow (In Wrapping Process) With High Tensile Tyre Chord & S.S. Wire Reinforced With Integral Rubber Flanges on both side With M.S. Backup Flanges -10 mm thick- Split Type Galvanized-Single Convolution Bellow As Per ANSI B 16.5 Class 150- Drilling Standard Temperature: 100 Deg. C Pressure : 10 kg/cm2 Test Pressure:16 kg/cm2 ID 8"XL 200 mm along with necessary fittings etc completed as directed.
33.1 | NDR | NDR | 200 mm dia | Nos | [21 empty] | 3 | 3 | 10350 | 31050
33.2 | NDR | NDR | 80 mm dia | Nos | [21 empty] | 2 | 2 | 5176 | 10352
34 | PWD-CSR |  | Earth work excavation over areas for foundation of tank, trenches, pits etc. in all soils, soft and hard rocks, upto depth 1.5 m including shoring and dewatering if necessary, dressing the sides, trimming and preparing the bed for foundation and refilling all round the foundation / tank (after testing) with selected excavated earth in layers not exceeding 250 mm thick, watering, consolidation and disposing off the surplus earth within a distance of 50 m etc, complete as per specifications & drawings, including spreading, levelling the surplus disposed earth in required grade / profile as directed by E-I-C. | [23 empty] | 0 |  | 0
34.1 | PWD-CSR | 16-1-7/PWD-CSR-22-23/Page No.238 | Excavation for foundation in earth, soil of all types, sand, gravel and soft murum (Lift Upto 1.50 Meter) Spec. No. : Bd.A 1 Page No.259 | Cum | [22 empty] | 0 | 232 | 0
34.2 | PWD-CSR | 16-1-6/PWD-CSR-22-23/Page No.238 | Excavation for foundation in hard murum (Lift upto 1.50 m). Spec. No. : Bd.A.2, P. No. 259. | Cum | [22 empty] | 12 | 270 | 3240
34.3 | PWD-CSR | 16-1-5/PWD-CSR-22-23/Page No.238 | Hard rock by chiseling, wedging, line drilling, etc. complete. (Lift upto 1.5 m) Spec No. : Bd.A 6 Page No.260 | Cum | [22 empty] | 5 | 1081 | 5405
35 |  |  | Flooring
35.1 | PWD-SSR | Sr.No.989/33.02/Page No.213-SSR-22-23 | Providing and laying Rough Shahabad Stone Flooring 40mm.to 45 mm. thick and of required width in plain/ diamond pattern on a bed of 1:6 C.M. including cement float, striking joints, pointing in cement mortar 1:3 curing and cleaning etc. etc. complete | RO /Sqm | [22 empty] | 0 | 791 | 0
35.2 | PWD-SSR | Sr.No.188/5.20/Page No.44/SSR-22-23 | Providing and fixing factory made Hydraulically pressed Mechanically vibrated and compacted precast inter locking cement concrete paving blocks 60MM thick in M-40 grade of approved size and shape for City streets, small /medium market roads, low volume roads, utility cuts on arterial roads etc. as specified and as per IS 15658:2006 including cost of all materials, manufacturing, curing, transportation of blocks to work site including loading, unloading and stacking as directed, laying paving blocks in position over prepared bed of natural sand / crushed sand of 50 mm thickness including necessary excavation in all strata’s, spreading blindge of fine sand over the prepared bed, compacting blocks by plate vibrator etc. complete. | RO / Sqm | [22 empty] | 0 | 1153 | 0
35.3 | PWD-SSR | Sr No.1021/33.34/BDM 3/Page No. 216/SSR-2022-2023 | Providing and laying in position flooring of telephone black / Amba White / Cat bary brown / Ruby red / Ocean Brown granite stone of approved shade and size 18 mm to 20 mm thick on bed 1:6 cement mortar including cement floats striking joints, pointing in C.M. 1:3 curing and cleaning etc. complete. | RO / Sqm | [22 empty] | 0 | 4005 | 0
B |  |  | FITTINGS & FIXTURES ETC.
1 | PWD-CSR |  | Supplying and installing cast iron double flange sluice valve of following size conforming to IS: 780, ISI mark having cast iron body and gun metal working parts with nut bolts, gaskets etc and tested to 1.5 times of working pressure in an approved manner. as per specification No. FF-VL/SV
1.1 | PWD-CSR | 13-7-14/PWD-CSR-22-23/Page No.220 | 100 mm dia | Nos | [21 empty] | 2 | 2 | 8753 | 17506
1.2 | PWD-CSR | 13-7-15/PWD-CSR-22-23/Page No.220 | 150 mm dia | Nos | [22 empty] | 3 | 13646 | 40938 | bar: A; B; C
1.3 | PWD-CSR | 13-7-16/PWD-CSR-22-23/Page No.220 | 200 mm dia | Nos | [21 empty] | 3 | 3 | 23265 | 69795
2 | PWD-CSR |  | Supplying and installing double flange NRV of size conforming to IS: 5312 (Part - I), ISI marks having cast iron body and gun metal working parts with nut bolts, gaskets etc and tested to 1.5 times of working pressure in an approved manner.
2.1 | PWD-CSR | 13-7-24/PWD-CSR-22-23/Page No.221 | 100 mm dia | Nos | [21 empty] | 2 | 2 | 8240 | 16480
2.2 | PWD-CSR | 13-7-26/PWD-CSR-22-23/Page No.221 | 200 mm dia | Nos | [21 empty] | 3 | 3 | 21297 | 63891
3 | NDR | NDR | Supplying and fixing of Pre Fabricated Tank of Syntehetic material. Tank Capacity 2,00,000 Ltrs. Warranty 5 Years or more. The tank to be mounted on solid metal frames of I-Beam of equivalent strenth. The tank to be placed a height of min 2.8 Mtrs above the ground level. The area betwen the ground level & the tank may be utilised as fire marshal. | Nos | [21 empty] | 3 | 1 | 1500000 | 1500000
|  |  | TOTAL OF PART – 1 - FIRE HYDRANT SYSTEM | [25 empty] | 6532128
[28 empty] | GST 18% | 1175783.04
[28 empty] | Total | 7707911.04

## 1.4-DSR-FSS
S. N. | PWD-BMC-SSR-NDR | SSR No. / P. No. | PARTICULARS | UNIT | A | A | A | A | A | B | B | B | B | B | C | C | C | C | C | D | D | D | D | D | COURTYARD | PUMPROOM | QTY | UNIT RATE (₹) | TOTAL AMOUNT (₹)
PART- 2 - SPRINKLER SYSTEM
1 | PWD-CSR | 13-12-1/PWD-22-23/Page No. 228 | Supplying and erecting 15mm (1/2") dia NBCM body chrome finished Quartizoid bulb sprinkler (Pendant type) having 68° C fixed temperature rating with deflector disc of conventional construction. as per specification No. FF-SPR | Each | A: 70; A: 49; A: 59; A: 18; B: 24; B: 61; B: 54; B: 20; C: 102; C: 82; C: 99 |  |  | 566 | 427 | 241682
2 | PWD-CSR | 13-12-1/PWD-22-23/Page No. 228 | Supplying and erecting 15mm (1/2") dia NBCM body chrome finished Quartizoid bulb sprinkler (Wall side) having 68° C fixed temperature rating with deflector disc of conventional construction. | Each | [22 empty] | 72 | 427 | 30744
3 | NDR |  | Supply, Installation, Testing & commissioning of Flexible drop with supports & approved makes - length - 01 Mtr, Type Braided, Shuold be able to withhold the System pressure & approved warranty | Each
3.1 | NDR | NDR (Quatation - Siddhi Tech Solution) | 1200 mm | Each | C: 102; C: 82; C: 99 |  |  | 12 | 1800 | 21600
3.2 | NDR | NDR (Quatation - Siddhi Tech Solution) | 1000 mm | Each | [22 empty] | 5 | 1650 | 8250
4 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supplying and fixing Rojas Plate for Sprinkler, as directed | Each | [22 empty] | 122 | 88 | 10736
5 | PWD-CSR |  | Supplying and erecting vane type water flow detector suitable for detecting flow of water in wet sprinkler pipe of main line or branch lines of following dia. having following features 1) Visual Switch Activation 2) Rugged Switch Assembly 3) Heavy duty Aluminium pipe Saddles 4) Durable Metal Enclosure 5) Steel U Bolts for Secure Mounting 6) Two SPDT (Single Pole Double Track) Synchronized Switches 7) Serviceable without Draining Pipes.
5.1 | PWD-CSR | 13-12-2/PWD-22-23/Page No.228 | 75 / 80mm dia | Each | [22 empty] | 2 | 7362 | 14724
5.2 | PWD-CSR | 13-12-3/PWD-22-23/Page No.228 | 100 mm dia | Each | [22 empty] | 9 | 8408 | 75672 | bar: A to A; B to B; C to C
6 | PWD-CSR |  | Supplying and installing G.I. Pipe above ground of 'C' Class ERW of following sizes conforming to IS:1239, along with necessary fittings and M.S. angle iron supports, with one coat of red oxide primer and two coats of Post office fire red enamel paint, duly tested to 1.5 times of working pressure, in an approved manner. as per specification no. FF-PP
6.1 | PWD-CSR | 13-6-7/PWD-22-23/Page No.219 | 150 mm dia | Rmt | [22 empty] | 72 | 2409 | 173448
7 | PWD-CSR |  | Supplying and installing G.I. Pipe underground of 'C' Class ERW of following sizes conforming to IS:1239, along with necessary fittings and M.S. angle iron supports, duly tested to 1.5 times of working pressure, in an approved manner. as per specification no. FF-PP
7.1 | PWD-CSR | 13-6-7/PWD-22-23/Page No.219 | 150 mm dia | Rmt | [22 empty] | 36 | 2409 | 86724
8 | PWD-CSR |  | Supply & installation of G.I. (C-class) pipe IS standard including cutting threading welding etc providing all required accessories confirming to IS 1239 standards like flanges, bends, tees, elbows, reducers, unions supporting with G.I clamps hangers etc including cuttings holes and chases in brick or RCC wall/slabs and making good the same to the approval of architect/ consultant including Painting with one coat of primer and two or more coats of red synthetic enamel paint of approved make and shade on the sprinkler pipes. (ISI mark). as per specification no. FF-PP
8.1 | PWD-CSR | 13-6-6/PWD-22-23/Page No.219 | 100 mm dia | Rmt | A: 18; A: 30; A: 24; B: 24; B: 36; B: 24; C: 24; C: 24; C: 30 |  |  | 160 | 1588 | 254080
8.2 | PWD-CSR | 13-6-5/PWD-22-23/Page No.219 | 80 mm dia | Rmt | A: 24; A: 30; B: 18; B: 14.57; C: 41; C: 30; C: 40 |  |  | 150 | 1116 | 167400
8.3 | PWD-CSR | 13-6-4/PWD-22-23/Page No.219 | 65 mm dia | Rmt | A: 26; A: 18; B: 6; B: 16.13; C: 19; C: 18; C: 18 |  |  | 90 | 893 | 80370
8.4 | PWD-CSR | 13-6-3/PWD-22-23/Page No.219 | 50 mm dia | Rmt | A: 7.37; A: 9.73; B: 9.2; B: 6.05 |  |  | 32.35 | 705 | 22806.75
8.5 | BMC | R3-ME-6-7-e BMC-2023/Page No.124 | 40 mm dia | Rmt | [22 empty] | 24 | 638 | 15312
8.6 | BMC | R3-ME-6-7-d BMC-2023/Page No.124 | 32 mm dia | Rmt | C: 29.52; C: 36; C: 36 |  |  | 101.52 | 554 | 56242.08
8.7 | PWD-CSR | 13-6-2/PWD-22-23/Page No.219 | 25 mm dia | Rmt | A: 154.97; A: 111.98; A: 131.1; A: 40.6; B: 51.36; B: 124.8; B: 101.1; B: 41.97; C: 162.8; C: 162.8; C: 162.8 |  |  | 1246.28 | 348 | 433705.44
9 | PWD-CSR | 3-11-77/PWD-22-23/Page No.70 | Carrying out core cutting of size 3" to 5" dia x 15" length in the C.C./rock/stone wall with the help of specialized core cutting machine in proper manner and finishing the site as original. | Job | [22 empty] | 10 | 7519 | 75190
10 | PWD-CSR | 13-8-13/PWD-22-23/Page No.223 | Supplying and erecting 20/25mm Ø G.M. air release cock, with necessary G.I. coupling to be fitted on top of Air vessel or on wet riser as per specification No. FF-FFA/ARV | Nos | [22 empty] | 3 | 840 | 2520 | bar: A; B; C
11 | PWD-CSR |  | Supplying & installing cast iron double flange butterfly valve of Following confirming to IS 13095 having cast iron body, FG 220 Nitrite rubber replaceable seat with moulded 'O' ring, C.I. powder coated disc flow control complete & tested to 1.5 times of working pressure in an approved manner. as per specification No. FF-VL/BFV
11.1 | PWD-CSR | 13-7-21/PWD-22-23/Page No.221 | 150 mm dia | Nos | [22 empty] | 4 | 6327 | 25308
11.2 | PWD-CSR | 13-7-20/PWD-22-23/Page No.221 | 100 mm dia | Nos | [22 empty] | 4 | 4121 | 16484
11.3 | PWD-CSR | 13-7-19/PWD-22-23/Page No.221 | 80 mm dia | Nos | [22 empty] | 8 | 3183 | 25464
12 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supplying and installing glycerine filled pressure gauge of 100 mm (4 inch) diameter, having range 0–14 kg/cm² (or 0–200 PSI), with stainless steel case and internals, bottom entry connection (3/8" or 1/2" BSP), and dual scale dial (kg/cm² and PSI) | Nos | [22 empty] | 11 | 4430 | 48730 | bar: A to A; B to B; C to C
13 | PWD-CSR | 13-8-15/PWD-22-23-/Page No.223 | Supplying and installing DANFOSS make pressure switch with 12/15 mm Ø isolation valve, G.I. nipple, elbow etc. in an approved manner as per specification No. FF-FFA/PS | Nos. | [21 empty] | 2 | 2 | 1763 | 3526
14 | PWD-CSR | 13-7-20/PWD-22-23/Page No.221 | Supplying & Installing cast iron double flange butterfly valve of size 100 mm dia. confirming to IS 13095 having cast iron body, FG 220 Nitrite rubber replaceable seat with moulded 'O' ring, C.I. powder coated disc flow control complete & tested to 1.5 times of working pressure in an approved manner. as per specification No. FF-VL/BFV | Nos. | [22 empty] | 9 | 4121 | 37089 | bar: A to A; B to B; C to C
15 | PWD-CSR |  | Supplying and installing cast iron Ball Type foot valve
15.1 | PWD-CSR | 13-7-2/PWD-22-23/Page No.219 | Supplying and installing cast iron foot valve ball type / flap type of size 100 mm dia with strainer for negative suction as per specification No. FF-VL/FV | RO/ Nos | [22 empty] | 0 | 6667 | 0
15.2 | PWD-CSR | 13-7-4/PWD-22-23/Page No.219 | Supplying and installing cast iron foot valve ball type / flap type of size200 mm dia with strainer for negative suction as per specification No. FF-VL/FV | RO/ Nos | [22 empty] | 0 | 31110 | 0
16 | PWD-CSR |  | Supplying and installing of following size end line 'Y' strainer for +ve suction, | [23 empty] | 0 |  | 0
16.1 | PWD-CSR | 13-7-6/PWD-22-23/Page No.220 | Supplying and installing 100 mm dia end line strainer for +ve suction as per specification No. FF-VL/ELS | Nos | [21 empty] | 2 | 2 | 6349 | 12698
16.2 | PWD-CSR | 13-7-8/PWD-22-23/Page No.220 | Supplying and installing 200 mm dia end line strainer for +ve suction as per specification No. FF-VL/ELS | Nos | [21 empty] | 3 | 3 | 21035 | 63105
17 | PWD-SSR |  | Providing and laying concrete pipes of I.S.NP. class of Following diameter in proper line, level and slope including necessary collars, excavation, laying, fixing with collars in cement mortar 1:1 and refilling the trench complete.
17.1 | PWD-SSR | Sr.No.1380/42.09/BDV 41/Page No. 274/SSR-2022-23 | 300 mm dia | RO/ Mtr | [22 empty] | 18 | 744 | 13392
18 | PWD-CSR |  | Supplying, Installing and Commissioning approved make Ball valve of following Sizes
18.1 | PWD-CSR | 13-7-32/PWD-22-23/Page No. 221 | Supplying & installing gun metal gate valve of size 25mm dia as per specification No. FF-VL/GV | Nos | [22 empty] | 11 | 1202 | 13222
18.2 | PWD-CSR | 13-7-33/PWD-22-23/Page No. 221 | Supplying & installing gun metal gate valve of size 50mm dia as per specification No. FF-VL/GV | Nos | [22 empty] | 2 | 1289 | 2578
19 | PWD-CSR |  | Road Breaking & Re-Surfacing
19.1 | PWD-CSR | 16-1-5/PWD-22-23/Page No.238 | Breaking and removing the existing bitumen pavement to full width and depth and disposal of the material to 2 kms, compaction with power roller etc complete. Spec. No. MORTH 2001 clause No. 202.3 P. No. 45 | Cum | [22 empty] | 2 | 1081 | 2162
19.2 | NDR | NDR (Quatation - Siddhi Tech Solution) | Making good the same after the work is satisfactorily completed Providing 50mm thick semi grout bituminous road surface including supplying all materials, preparing the existing road surface, laying the required thickness of metal layer, heating and spraying bitumen, spreading chips, laying seal coat and compacting complete as directed by Engineer in charge. (By using Bulk Asphalt 60/70 grade) Spec. No. Rd.60 Page No.232. | Sqm | [22 empty] | 2 | 531 | 1062
20 |  |  | Removing and Demolishing
20.1 | PWD-SSR | Sr.No.1557/46.19/BDW 8/Page No. 297 (Civil SSR) 2022-23 | Removing Shahabad or Tandur stones /Cement tiles/ Pever Block / Marble mosaic tiles from floor without bed concrete including stacking the materials as directed with all leads, lifts, complete. As directed by Engineer in charge. | RO/Sqm | [22 empty] | 0 | 45 | 0
20.2 | PWD-SSR | Sr.No.1550/46.12/BDW 8/Page No. 296/SSR-22-23 | Removing lime or lean cement concrete including stacking the spoils as directed with all leads, lifts, complete. As directed by Engineer in charge. | RO/Cum | [22 empty] | 0 | 558 | 0
21 | NDR | NDR (Quatation - Siddhi Tech Solution) | Disposing of dismantling material of reinforced cement concrete stone / brick masonry from work site to 50m beyond the building area. Disposing of the surplus excavated materials by mechanical transport to the lead upto 2 km over the initial lead of 50 m including loading, unloading, spreading, leveling etc., As directed by Engineer in charge. | RO/Cum | [22 empty] | 0 | 287 | 0
22 | NDR | NDR (Quatation - Siddhi Tech Solution) | Fabrication, supply and installation of MS support as required but not covered under specific items as per drawings, specifications and as instructed by E-I-C. Material shall conform to IS-2062. | KG | [22 empty] | 200 | 150 | 30000
23 | PWD-CSR | 16-3-5/PWD-22-23/Page No.239 | Providing Cement concrete foundation for pump in 1:2:4 with required size and length of foundation bolts and nuts as per design and drawing etc compel (cost with wooden box is included). Etc completed as Directed | Cum | [22 empty] | 3 | 5011 | 15033
24 | PWD-SSR | Sr.No.381/11.04/CD 3B/Page No.81/SSR22-23 | Providing and laying is situ, cement concrete in 1:4:8 of trap / granite / quartzite / gneiss metal for foundation and bedding including bailing out water, formwork, compacting, finishing if required and curing etc. complete as Directed | Cum | [22 empty] | 3 | 5780 | 17340
25 | PWD-CSR | 13-6-10/PWD-22-23/Page No.219 | Providing coating of Bitumen Paint & 4mm thick Wrapping as per IS 10221 for underground 150 mm Ring Main of Fire Fighting System. | Mtr | [22 empty] | 12 | 345 | 4140
26 | PWD-SSR | Sr.No.1384/42.13/BDV 43/Page No.275/SSR-22-23 | Providing & constructing Brick Masonry in cement mortar 1:6 for Inspection Chamber 90cm x 45cm including 1:4:8 cement concrete foundation 1:2:4 cement concrete channels half round S.W.G. pipes, with plastering Brick Masonry inside and outside with cement mortar 1:4 and inside neat cement finish including 75mm thick RCC cover etc. complete (depth upto 1.20m).Bd.V.43 Page No.574. | Nos | [22 empty] | 3 | 10777 | 32331
27 | NDR | NDR | Supplying and fixing of Expansion Bellow Valve Neoprene Rubber Expansion Bellow (In Wrapping Process) With High Tensile Tyre Chord & S.S. Wire Reinforced With Integral Rubber Flanges on both side With M.S. Backup Flanges - 10 mm thick - Split Type Galvanized - Single Convolution Bellow As Per ANSI B 16.5 Class 150- Drilling Standard Temperature : 100 Deg.C Pressure : 10 kg/cm2 Test Pressure : 16 kg/cm2 ID 8" X L 200 mm along with necessary fittings etc completed as directed.
27.1 | NDR | NDR (Quatation - Siddhi Tech Solution) | 200 mm dia | Nos | [21 empty] | 1 | 1 | 10350 | 10350
27.2 | NDR | NDR (Quatation - Siddhi Tech Solution) | 80 mm dia | Nos | [21 empty] | 1 | 1 | 5176 | 5176
28 | PWD-CSR |  | Earth work excavation over areas for foundation of tank, trenches, pits etc. in all soils, soft and hard rocks, upto depth 1.5 m including shoring and dewatering if necessary, dressing the sides, trimming and preparing the bed for foundation and refilling all round the foundation / tank (after testing) with selected excavated earth in layers not exceeding 250 mm thick, watering, consolidation and disposing off the surplus earth within a distance of 50 m etc, complete as per specifications & drawings, including spreading, leveling the surplus disposed earth in required grade / profile as directed by E-I-C. | [23 empty] | 0 |  | 0
28.1 | PWD-CSR | 16-1-7/PWD-22-23/Page No. 238 | Ordinary Soils of all types sand, gravel and soft murum (Lift Upto 1.50 Meter) Spec. No. : Bd.A 1 Page No.259 | RO/Cum | [21 empty] | 18 | 3 | 232 | 696
28.2 | PWD-CSR | 16-1-6/PWD-22-23/Page No. 238 | Hard murum (Lift upto 1.50 m). Spec.No. : Bd.A.2, P. No. 259. | RO/Cum | [21 empty] | 20 | 3 | 270 | 810
28.3 | PWD-CSR | 16-1-5/PWD-22-23/Page No. 238 | Hard rock by chiseling, wedging, line drilling, etc. complete. (Lift upto 1.5 m) Spec No. : Bd.A 6 Page No.260 | RO/Cum | [22 empty] | 0 | 1081 | 0
29 | PWD-SSR |  | Flooring | [23 empty] | 0 |  | 0
29.1 | PWD-SSR | Sr.No.989/33.02/Page No.213-SSR-22-23 | Providing and laying rough Shahabad Stone Flooring 40 mm. to 45 mm. thick & of required width in plain/diamond pattern on a bed of 1:6 C.M. including cement float, striking joints, pointing in cement mortar 1:3 curing and cleaning etc. complete. | RO/Sqm | [22 empty] | 0 | 791 | 0
29.2 | PWD-SSR | Sr.No.188/5.20/Page No.44/SSR-22-23 | Providing and fixing factory made Hydraulically pressed Mechanically vibrated and compacted precast inter locking cement concrete paving blocks 80MM thick in M-40 grade of approved size and shape for City streets, small /medium market roads, low volume roads, utility cuts on arterial roads etc. as specified and as per IS 15658:2006 including cost of all materials, manufacturing, curing, transportation of blocks to work site including loading, unloading and stacking as directed, laying paving blocks in position over prepared bed of natural sand / crushed sand of 50 mm thickness including necessary excavation in all stratas, spreading blindge of fine sand over the prepared bed, compacting blocks by plate vibrator etc. complete. | RO/Sqm | [22 empty] | 0 | 1153 | 0
29.3 | PWD-SSR | Sr No.1021/33.34/BDM 3/Page No. 216/SSR-2022-2023 | Providing and laying in position flooring of telephone black/AmbaWhite/Catbarybrown/Rubyred/Ocean Brown granite stone of approved shade and size 18mm to 20mm thick on bed 1:6 cement mortar including cement floats striking joints, pointing in C.M. 1:3 curing and cleaning etc. complete. | Sqm | [22 empty] | 0 | 4024 | 0
| PWD-CSR |  | FITTINGS & FIXTURES ETC. | [23 empty] | 0 |  | 0
1 | PWD-CSR |  | Supplying and installing cast iron double flange sluice valve of following size conforming to IS: 780, ISI mark having cast iron body and gun metal working parts with nut bolts, gaskets etc and tested to 1.5 times of working pressure in an approved manner. as per specification No. FF-VL/SV | [23 empty] | 0 |  | 0
1.1 | PWD-CSR | 13-7-14/PWD-22-23/Page No.220 | 100 mm dia | Nos | [21 empty] | 2 | 2 | 8753 | 17506
1.2 | PWD-CSR | 13-7-15/PWD-22-23/Page No.220 | 150 mm dia | Nos | [21 empty] | 0 | 3 | 13646 | 40938 | bar: A; B; C
1.3 | PWD-CSR | 13-7-16/PWD-22-23/Page No.220 | 200 mm dia | Nos | [21 empty] | 6 | 3 | 23265 | 69795
2 | PWD-CSR |  | Supplying and installing double flange NRV of size conforming to IS: 5312 (Part - I), ISI marks having cast iron body and gun metal working parts with nut bolts, gaskets etc and tested to 1.5 times of working pressure in an approved manner.
2.1 | PWD-CSR | 13-7-24/PWD-22-23/Page No.221 | 100 mm dia | Nos | [22 empty] | 4 | 8240 | 32960
2.2 | PWD-CSR | 13-7-26/PWD-22-23/Page No.221 | 200 mm dia | Nos | [21 empty] | 2 | 4 | 21297 | 85188
3 | PWD-CSR | 13-1-6/PWD- 22-23/Page No. 210 | Supplying, installation, testing and commissioning of main fire pump(MFP/EP) suitable for water discharge of 2280 to 2850 LPM at 120 to 90 m head driven by electric motor 415 volts, 3 phase 50 Hz, AC supply of 75kW or of suitable kW capacity for manual/automatic operation and consisting of following: (a) Horizontal type, single stage, centrifugal/split casing pump of cast iron body & bronze impeller with stainless steel shaft(SS410 grade), mechanical seal conforming to IS 1520. (b) Squirrel cage induction motor, TEFC, synchronous speed 3000 RPM, suitable for operation with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Erected on provided suitable size cement concrete foundation duly plastered with anti vibration pads with perfect aligning, proper levelling complete pump set with accessories duly painted with two coats of synthetic enamel paint of fire red colour over a coat of primer (ISC code 536 as per IS 2932 of 2003) complete, as per specification no. FF-MFP/SSC/EP | Each | [20 empty] | 2 | 2 | 2 | 409749 | 819498
4 | PWD-CSR | 13-2-3/PWD-22-23/Page No.212 | Supplying installing, testing, commissioning of Jockey Pump of 240 LPM at 105 m head, 3 ph. 415 A.C.15 HP, (11 kW) or of suitable HP with 2900 RPM C.1 casing single stage (mono block) with Bronze impeller, Bronze working parts (EN-8) shaft (C-40) and directly coupled to suitable capacity H.P motor, 'B' class insulation squirrel cage induction motor working on 3 ph. 440 A.C. Both Pump & Motor are to be mounted on common base plate along with suitable rigid foundation, nut bolts, with coupling guards and antivibration rubber pads in an approved manner, as per specification No. FF-MFP/JP (Similar to Kirloskar KDS 844+/MBH make.). | Nos | [20 empty] | 2 |  | 2 | 105613 | 211226
5 | BMC | R3-ME-15-3-a/BMC-23/Page No.199 | Supplying installing, testing, commissioning of Booster Pump of 450 LPM at head, 10 HP or of suitable HP with suitable Stages as per specification No. FF-MFP/BP | Each | [20 empty] | 2 |  | 4 | 81147 | 324588
6 |  | 2003-01-13 | Supplying and installing, testing, perfect aligning and proper levelling and commissioning of fire service main pump, (for Sprinkler) multistage, of 2800 LPM (Litres/min.) at 75 mtr head centrifugal type, 75 HP, (55 kW) or of suitable HP as per specification No. FF-MFP/MSC | RO/Each2 | [20 empty] | 1 |  | 0 | 317455 | 0
7 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supply, installation, testing and commissioning of Diesel Engine driven fire pump suitable for automatic operation comprising of the following and conforming to BS 649/IS 10002 all amended upto date complete as required. a). Horizontal, split casing, high pressure centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and SS (304) shaft with mechanical seal, capable for delivering 1450 LPM capacity @ 56 M head to ensure a minimum pressure of 3.5 Kg /Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority). Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | Each | [20 empty] | 1 |  | 1 | 550000 | 550000
| NDR |  | b. The tank shall be fitted with Magnetic oil level indicator, MH with cover, drain valve, air vent including structural supports (painted with approved shade), 2 Nos. x 12 volt battery, heat exchanger with necessary piping connections & fittings, flexible coupling, coupling guard & exhaust pipe connection complete as required.
| NDR |  | c. Common base plate for (a) and (b) from M.S. channel of required size.
| NDR |  | d. Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by contractor) complete with ant vibration arrangement of cushy foot mountings.
| NDR |  | Full Set as above
8 | NDR | NDR (Quatation - Siddhi Tech Solution) | Providing Supplying erecting and testing and commissioning of Fuel Tank (500 Ltr Capacity) with stand, fuel piping with valves and other accessories as per design and drawing etc complete.fuel tank to be handed over by contractor. | Nos | [20 empty] | 1 |  | 1 | 11500 | 11500
9 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supply, Fabricating and Fixing of Florescent Type Safety Signs and Exit Signs on all strategic location as per the IS 123449 & IS 12407. | Lot | 3 | 10 | 10 | 10 |  | 5 | 10 | 10 | 10 |  |  | 10 | 10 | 10 |  |  | 4 | 4 | 4 |  |  |  | 1 | 20000 | 20000
C | NDR | NDR (Quatation - Siddhi Tech Solution) | FIRE EXTINGUISHERS
1 | NDR | NDR (Quatation - Siddhi Tech Solution) | Ceiling Mounted Automated fire Extinguishers
1.1 | NDR | NDR (Quatation - Siddhi Tech Solution) | Supplying and erecting 9 Ltr Mechanical Foam Extinguisher | Nos | [22 empty] | 2 | 2156 | 4312
1.2 | PWD-CSR | 13-15-1/PWD-22-23/Page No.228 | S u p p l y i n g & erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg. capacity cartridge type conform to IS 2878 /15683 complete erected with necessary clamp made from 50 x 6 mm. M. S. flat with nut & bolts routed in wall complete | Nos | [22 empty] | 6 | 9902 | 59412
1.3 | BMC | R3-ME-15-30-c /BMC-2023/Page No-206 | Supplying and erecting ABC powder type fire extinguisher as per IS : 13849 /15683 of 6 kg capacity with necessary clamp for erection on Wall | No | [22 empty] | 6 | 2156 | 12936
E |  |  | Electrical Works
1 | NDR | NDR (Quatation - Siddhi Tech Solution) | Fire Pump Panel (Electrical) (Suitable for all above pumps) and as required. | Set | [20 empty] | 1 |  | 1 | 525300 | 525300
| NDR | NDR | Supplying, erecting, testing and commissioning cubicle pattern electrical control panel made of 14 /16 / 18 / 20 SWG MS Sheet duly painted with 2 coats of enamel paint,
| NDR | NDR | Electrical switchboards, powder coated floor mounting, front operated front ccess cubicle type, totally enclosed, with IP-42 protection with inged and lockable doors. It shall be fabricated from 2 mm thick
| NDR | NDR | Notes
| NDR | NDR | 1) All G.A. & fabrication drawings shall be got approved from the E.I.C. Necessary touch up painting may be done at site, incase if required. The scope includes all tests as specified in department's specification, relevant I.S. and as required by E.I.C, shall have to be performed at factory & at installation site and shall be included in the quoted rate.
| NDR | NDR | 2) The equipment shall be designed to ensure complete safety during operation inspection, connection of cables etc.
| NDR | NDR | 3) Control wires shall be of 1.1 KV 1.5 sq.mm FRLS copper wires and neatly bunched separately and adequately supported
| NDR | NDR | so as to prevent sagging and strain on termination.
| NDR | NDR | 4) A minimum of 10% spare terminals shall be provided on
| NDR | NDR | each terminal block for future requirement.
| NDR | NDR | 5) All metallic parts of the equipment not carrying current shall be earthed with copper material
| NDR | NDR | 6) All concealed hinged doors and covers shall be provided with suitable flexible earthing connections.
| NDR | NDR | 7) The size of the earth bus chosen shall be to withstand full fault current of 25 KA
| NDR | NDR | 8) Earth bus bar shall be supported at suitable intervals.
| NDR | NDR | 9) All the current transformers shall be resin cast type class-I only.
| NDR | NDR | 10) Name of fabricator, G.A. & detailed fabrication drawing and short circuit forces and temp rise calculation for panel shall be
| NDR | NDR | submitted for dept's approval.
| NDR | NDR | 11) Bimetallic washers shall be used for all aluminium to copper joints & it shall be of approved make & quality.
| NDR | NDR | 12) Indication lamps shall be heavy duty cluster type LED.
| NDR | NDR | 13) All Outgoing feeders shall have 'ON' indication lamps.
| NDR | NDR | 14) All neutrals shall be isolatable type.
| NDR | NDR | 15) Power cabling between motor and starter shall be measured separately. Control cabling between panel and tank shall be measured separtaely. However, any other control / power wiring / cabling, if required is in the scope of this item.
| NDR | NDR | 16) Multiplication of level switches using relays / contactors and necessary control cable for control of both main and standby domestic & flushing water supply pumps shall be in the scope of the bidders.
2 | PWD-CSR |  | Cables
2.1 | PWD-CSR | 7-1-20/PWD-22-23/Page No.127 | Supplying, erecting & terminating XLPE armoured cable 3½ core 120 sq. mm. aluminium conductor with continuous 12.97 sq. mm. (8 SWG) G.I. earth wire complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe as per specification no. CB-LT/AL | Mtr | [21 empty] | 36 | 130 | 754 | 98020
2.2 | PWD-CSR | 7-1-30/PWD-22-23/Page No.128 | Supplying, erecting & terminating XLPE armoured cable 4 core 25 sq. mm. aluminium conductor with continuous 5.48 sq. mm. (12 SWG) G.I. earth wire complete erected with glands & lugs, on wall/ trusses/pole or laid in provided trench/ pipe as per specification no. CB-LT/AL | Mtr | [21 empty] | 48 | 48 | 261 | 12528
2.3 | PWD-CSR | 7-2-33/PWD-22-23/Page No.132 | Supplying, erecting & terminating XLPE armoured cable 4 core 10 sq. mm. copper conductor continuous 5.48 sq. mm. (12 SWG) G.I. earth wire complete erected with glands & lugs, on wall/ trusses/ pole or laid in provided trench/ pipe as per specification no. CB-LT/CU | Mtr | [21 empty] | 24 | 24 | 603 | 14472
2.4 | PWD-CSR | 13-9-13/PWD-2022-23/Page No.224 | Supplying, installing, testing and commissioning FR, XLPE armoured cable 12 core 1.5 sq.mm. copper conductor complete erected on wall/ ceiling complete as per specification no. CB-LT/CU | Mtr | [21 empty] | 36 | 36 | 322 | 11592
2.5 | PWD-CSR | 9-2-3/PWD-22-23/Page No.160 | Supplying and erecting GI strip of required size used for earthling on wall and/or any other purpose with necessary GI clamps fixed on wall painted with bituminous paint in an approved manner with joints required. As per specification no EA-EP. | KG | [21 empty] | 120 | 20 | 222 | 4440
[27 empty] | 0 |  | 0
|  |  | TOTAL OF PART – 2- SPRINKLER SYSTEM | Total | [24 empty] | 5078113.27
[28 empty] | GST 18% | 914060.3886
[28 empty] | Total | 5992173.6586

## 1.4-DSR-FAS
PART- 3 - SMOKE DETECTION & FIRE ALARM SYSTEM (ADDRESSABLE) & PUBLIC ADDRESS SYSTEM
S. N. | PWD-BMC-SSR-NDR | SSR No. / P. No. | PARTICULARS | UNIT | A | A | A | A | A | B | B | B | B | B | C | C | C | C | C | D | D | D | D | D | COURTYARD | PUMPROOM | QTY | UNIT RATE (₹) | TOTAL AMOUNT (₹)
1 | NDR | NDR | Main Fire Alarm Control Panel
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Microprocessor based Net-workable Analogue Addressable Fire Alarm Control Panel. The Panel shall be compliant with EN54-2, EN54-4 and approved by LPCB. The Fire Alarm Control Panel shall have expandable capacity from 2 loops to 16 loops. The Panel must have Full colour 800 x 480 LCD with resistive touch screen and automatic backlight dimming. The Panel must also have the capability to take Addressable AnalogueWired and Wireless Devices on same loop. Each loop shall have a capacity of 127 analogue Addressable devices and 127 Base sounders/Base Sounder Beacons. The panel shall have an event log of minimum 10,000 events @ 1 second resolution, Filterable and Printable. The Panel shall have Three access levels. Panel shall support upto 5000 Cause & Effects entries, with upto 20,000 inputs controlling & 20,000 Controlling outputs across the network. The Panel shall have capability for Peer to Peer networking through RS485 network card. The Panel must have 4 inbuilt programmable sounder circuits, each circuit rated at 2.5A.The Panel must have inbuilt 3 programmable inputs and 5 inbuilt programmable relay outputs. The Panel shall have up to sub-addressable 512 programmable Inputs/Outputs via optional RS485 COMMS serially connected expansion cards. The Panel shall have 240 V AC power supply along with automatic Battery Charger. The Panel shall be fully expandable via common plug in loop driver boards. The user shall have a choice of using the panel with 5.25 Amp or 10.25 Amp power supply unit which is inbuilt in the FACP and should be approved to EN54-4. The Panel shall have configurable via USB port to PC or memory stick. The Panel shall have dedicated RS232 serial port for optional printer. Approved by LPCB. | No. | [22 empty] | 1 | 375000 | 375000 | bar: A; D
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Network Module. The Module shall connect Panels and Repeator Panels through RS485. The Module shall use RS485 data at a Baud rate of 115200 Bauds. The Network Module must be configured Master/Slave, Multiple Master/Slave and Peer to Peer net W\working. | No | [22 empty] | 1 | 102180 | 102180
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Local LCD Control Repeater Panel to be integrated with Fire Alarm Control Panel. Panel should have 8 lines of 40 characters graphic LCD and shall be compliant with EN54-2, EN54-4 and Approved by LPCB. | No | [22 empty] | 1 | 112211 | 112211
2 | PWD-CSR |  | Analogue Addressable Optical smoke detector | [23 empty] | 0 |  | 0
| PWD-CSR | 13-9-3/PWD-CSR-22-23/Page No.224 | SITC of Analogue Addressable Smoke Sensor which is fully compatible with Analogue Addressable Protocol, having removable high performance chamber with Twin fire LED's allow 360 degree viewing, User selectable sensitivity modes 1% to 4.5% obs/m, Incorporate Optical elements, lock mechanism (sensor to base), Electronically addressed, Pulsing/non-pulsing controlled from panel. Approved by LPCB & VdS with back box. | Nos. | A: 12; A: 38; A: 37; A: 14; B: 6; B: 37; B: 32; B: 9; C: 48; C: 49; C: 42 |  |  | 324 | 1730 | 560520
3 | PWD-CSR |  | Analogue Addressable Multi sensor (Photo + Heat) smoke detector | [23 empty] | 0 |  | 0
| PWD-CSR | 13-9-2-NEW/PWD-CSR-22-23/Page No.224 | SITC of Analogue Addressable Multi- Sensor which is fully compatible with Analogue Addressable Protocol,having removable high performance chamber with Twin fire LED's allow 360 degree viewing, User selectable sensitivity modes 1% to 4.5% obs/m, Incorporate Optical and dual Heat elements, lock mechanism (sensor to base), Electronically addressed, Pulsing/non-pulsing controlled from panel. Approved by LPCB & VdS. | Nos. | [22 empty] | 0 | 2255 | 0
4 | NDR |  | AnalogueAddressable Manual Call Point
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Analogue Addressable Manual Call Point with Integral Short Circuit Isolator, Analogue Addressable Protocol having, Bi-coloured status LED (red for alarm, amber for (short-circuit), Non-frangible element fitted as standard (conforms to EN54), pulsing/non-pulsing can selectable via panel, Electronically addressed, Approved by LPCB. | Nos. | 2 | 4 | 5 | 1 |  | 2 | 4 | 4 | 1 |  |  | 6 | 8 | 7 |  |  | 1 | 1 | 1 |  |  |  | 20 | 4370 | 87400
5 | NDR |  | AnalogueAddressable Hooter cum Strobe | [23 empty] | 0 |  | 0
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Intelligent Loop Powered Wall Sounder Beacon, Variable Sound Output 90 ~ 102 dB(A) (±2 dB(A)) output at 1 metre, High Intensity LED technology, 51 User-Selectable Tones (all tones EN54-3 compatible). Approved by LPCB & VdS. | Nos. | 2 | 3 | 4 | 1 |  | 1 | 2 | 4 | 1 |  |  | 6 | 6 | 6 |  |  | 1 |  | 1 |  |  |  | 19 | 4537 | 86203
6 | NDR | NDR | Isolator | [23 empty] | 0 |  | 0
| NDR | NDR (Quatation - Siddhi Tech Solution) | SITC of Short Circuit Isolator. The device shall have ability to locate between any devices on the SLC loop, Indicate of a single short circuit by a yellow LED, UL Approved | Nos. | [22 empty] | 3 | 2050 | 6150 | bar: A; B; C
| NDR |  | (Additionally separate Isolator modules will installed only if required) | [23 empty] | 0 |  | 0
7 | NDR | NDR | Response Indicator | [23 empty] | 0 |  | 0
| PWD-CSR | 13-9-9/PWD-CSR-22-23/Page No.224 | Supplying, erecting and testing of response indicators as per specification .and as directed. | Noa. | A: 12; A: 38; A: 37; A: 14; B: 6; B: 37; B: 32; B: 9; C: 48; C: 49; C: 42 |  |  | 270 | 207 | 55890
8 | PWD-CSR |  | FRL Armoured Cable | [23 empty] | 0 |  | 0
| PWD-CSR | 13-9-11 PWD-2022-23 Page No. 242 | Supplying, installing, testing and commissioning FR, XLPE armoured cable 4 core 1.5 sq.mm. copper conductor complete erected on wall/ ceiling complete as per specification no. CB-LT/CU | Mtrs. | 144 | 456 | 444 | 168 |  | 72 | 444 | 384 | 108 |  |  | 576 | 588 | 504 |  |  |  |  | 80 |  |  |  | 2968 | 135 | 400680
9 | PWD-CSR | 7.-11.-6 | Cable Tray | [23 empty] | 0 |  | 0
| PWD-CSR | 7.-11.-6/PWD-2022-23 Page No. 144 | Providing & erecting Hot dipped Galvanised Perforated type Cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 150 mm width & 75 mm height complete with necessary coupler plates & hardware in approved manner. etc complete as directed | Mtrs. | [22 empty] | 500 | 614 | 307000
10 | PWD-CSR | 3.-11.-77./PWD-2022-23 Page No. 70 | Carrying out core cutting of size 3" to 5" dia x 15" length in the C.C./rock/stone wall with the help of specialized core cutting machine in proper manner and finishing the site as original. | BLDG | [22 empty] | 40 | 7519 | 300760
|  |  | TOTAL OF PART – 3- SMOKE DETECTION & FIRE ALARM | Total | [24 empty] | 2393994
[28 empty] | GST 18% | 430918.92
[28 empty] | Total | 2824912.92
11 |  |  | Public address and Voice Alarm Control Panel
| NDR | NDR | Digital microprocessor-controlled voice alarm compact amplifier for voice alarm, announcements and background music. Integrated audio inputs, 8-level priority control, voice alarm control, power amplifier, circular dial and complete monitoring according to VDE 0828-1, EN 54-16 and VDE 0833-4. 6 switchable and adjustable volume speaker outputs with a total of 240 Watt nominal power output. Three microphone / audio carrier inputs with switchable sensitivity as well as two stereo audio carrier inputs with volume control and tone control on front panel, one input switchable sensitivity and volume control back to prevent an intentional or unintentional adjustment, two speaking bus lines for up to four external stations. Front mounted acoustic and electronically monitored fire brigade microphone (fist microphone) with control panel for controlling the alarm: emergency one and out, range selection, selection of evacuation and warning text. Fault indication with plain text display of the occurred error, acoustic signal and reset button. Password-protected setting the equalizer settings, language, password many more. and display relevant system information via menu on alphanumeric two-line display. LAN connection for system programming and read out of the log with detailed event and error messages to diagnose locally or to remote diagnosis. 8 universally usable inputs and 8 universally usable control outputs; 6 separate inputs for alarm control of the BMZ with switchable monitoring, one with 24-volt control (polarity); three separate control outputs with relay contacts for feedback to the BMZ: collective fault signal (changeover contact), emergency (changeover contact) and activated CPU off (make contact). Each line output a switching relay for example external volume control in 3- and 4-wire technology. An appropriate additional amplifier can be used as a rescue and announcement enhancer, in the second case, announcements are made without the interruption of background music in durchsagelose areas can be made. The monitoring of the additional amplifier is taken over by the compact amplifier. Extension of the system up to 60 areas with suitable extension amplifiers possible. | No | [22 empty] | 1 | 360000 | 360000
12 |  |  | Booster Amplifier
| NDR | NDR | The booster amplifier shall operate on 220 – 240 V AC or 24 V DC power, and shall control and mix 1 balanced (screw terminal) Line in and 1 unbalanced (screw terminal) 100 V Line inputs. Outputs shall be balanced Loop out and balanced high and low impedance (floating) Speaker out. The amplifier shall meet the following performance criteria: Power output shall be 240 W at less than 1% THD (at 1 kHz, 1/3 rated power). Frequency response shall be 50 Hz to 20 kHz (+/-3 dB), with an S/N ratio of over 60 dB. Bass Tone Control shall be +/-10 dB at 100 Hz, and Treble Tone Control shall be +/-10 dB at 10 kHz. It shall be possible to bypass the master volume to make emergency announcements. Power, signal and peak indicators, and fan cooling ventilation shall be provided. The panel shall be ABS black resin, and the case black steel plate. Dimensions shall be 420 (W) x 100.9 (H) x 351.3 (D) mm, and weight 13.2kg. | [23 empty] | 1 | 78000 | 78000
13 | NDR | NDR | DIGITAL BOOSTER AMPLIFIER
| NDR | NDR | The booster amplifier shall operate on 100 - 240 V AC, 50/60Hz or 24 V DC power, and shall control and mix 1 balanced (screw terminal) Line in and 1 unbalanced (screw terminal) 100 V Line inputs. Outputs shall be balanced Loop out and balanced high and low impedance (floating) Speaker out. The amplifier shall meet the following performance criteria: Power output shall be 480 W at less than 1% THD (at 1 kHz, 1/3 rated power). Frequency response shall be 50 Hz to 20 kHz, with an S/N ratio of over 70 dB or better. Bass Tone Control shall be +/-10 dB at 100 Hz, and Treble Tone Control shall be +/-10 dB at 10 kHz. It shall be possible to bypass the master volume to make emergency announcements. Power, signal and peak indicators, and fan cooling ventilation shall be provided. The panel shall be ABS black resin, and the case black steel plate. | [23 empty] | 1 | 142000 | 142000
14 | NDR | NDR | REMOTE MICROPHONE
| NDR | NDR | Digital paging microphone with 15 programmable buttons with activation indicator led for area and text option from the text store. Digital control signals, audio signals, and power supply via bus line. Input socket for external power supply, socket for connecting a headset speaking with preload for electret microphones. Integrated Mic Preamps with switchable compressor and adjustable microphone sensitivity, floating balanced output. Automatic triggering of a pre and/or post gongs from 4 different 1-4 sound effects by the talk button can be programmed, display by LED during the Gong. Operational, engaged and talking advertisement for activation. Intercom station without additional accessories as a built-in intercom can be used. The number of buttons can be increased through a keyboard extension. Monitoring speaking points connecting to the ELA management amplifier. Indicator for connection failures to the ELA management system. Output level: 0 dBV into 600 ohm Frequency response: 100 Hz to 19kHz Connection cable: Category 5 cable with RJ45 connectors, maximum length: 800m | [23 empty] | 1 | 64000 | 64000
15 | NDR | NDR | CEILING MOUNT SPEAKER
| NDR | NDR | The ceiling mount loudspeaker shall be an integrated cone driver, line transformer and baffle (grille) assembly. The driver shall be a 16cm (6") diameter cone type with 8ohm nominal impedance and a ferrite magnet. Power handling shall be 6 W (15 W program) with a frequency response from 65 – 18 KHz and sensitivity of 90 dB SPL at 1 W input measured at a distance of 1m. The line transformer shall accept 70 V and 100V inputs with taps for 1 W, 3 W and 6 W with an output impedance of 8 ohms. The baffle shall be made of polypropylene resin and grille shall be surface-treated steel plate net with an off-white color (RAL9010). With two spring clamps mounted at the opposite side of the baffle for easily assembly.(The contractor to use back box as required) | [23 empty] | 100 | 1900 | 190000
16 | NDR | NDR | WALL MOUNT SPEAKER 6W BLK
| NDR | NDR | The speaker shall be a 5" (12cm) cone type enclosure suitable for wall mounting with a supplied plug-in speaker receptacle accessory. The input connector shall be an M4 screw terminal, with an 11 mm distance between barriers. The speaker impedance shall be 1.7kohm (6W) or 3.3kohm (3W) for a 100V line, and 1.7kohm (3W) or 3.3kohm (1.5W) for a 70V line. The output sound pressure level at a distance of 1m with a 1W input level applied shall be 90 dB SPL. The speaker shall have a frequency response of 120 – 18,000Hz (-20dB). The speaker enclosure shall be constructed of fire-resistant HIPS resin. The grille shall be constructed of surface-treated steel plate net. | [23 empty] | 45 | 7400 | 333000
17 | NDR | NDR | PAGING HORN SPEAKER
| NDR | NDR | Weather-resistant pressure chamber loudspeaker compliant with IP65 in 100 V design, oval horn made of powder-coated aluminium, driver cover made of ABS plastic, swivelling bracket made of stainless steel for precise alignment of the speaker, rear selector switch for power matching Rated power: 15 W Power matching: 15W, 10W, 5W, 3W Degree of protection: IP65 Frequency response: 280 – 12,500 Hz Sound pressure (1W/1m): 109 dB (Peak 112dB) | [23 empty] | 8 | 11000 | 88000
18 | NDR | NDR | ATTENUATOR
| NDR | NDR | The Attenuator is a flush-mounted wall attenuator and uses a transformer which allows connection of a wide range of loads (30 W or less). Volume can be adjusted in eight steps. Wall mounting back Box as required | [23 empty] | 15 | 7500 | 112500
1367500
[28 empty] | GST | 246150
[28 empty] | Total | 1613650
[28 empty] | Total | 4438562.92

## 1.4-DSR-PP
PART- 4 - SITC OF PASSIVE PROTECTION - ITEMS - FRD 120 (METAL)
S. N. | SSR No. / P. No. | PARTICULARS | UNIT | A | A | A | A | A | B | B | B | B | B | C | C | C | C | C | D | D | D | D | D | COURTYARD | PUMPROOM | QTY | UNIT RATE (₹) | TOTAL AMOUNT (₹)
1 | NDR | Fire Door (Metal) 120 min rating
| NDR | For Single / Double Leaf Door (Including Frame, Shutter & Fastners) confirming to BS - 476, Part 22 and IS : 3614 Part II, with thick galvanised steel sheet. The frame & shutter are finished with Powder Metal Single Frd Door 120min Rating. As per the below mentioned specifications:- Type - Fire Resistant Double Leaf, MOC - Metal, MS, Size of wall opening Width: 1500 mm, Height: 1800 mm (The contractor to take detailed measurement & opening pattern approval from client) Door leaf Size - Includes both leaf Width: 1360 mm, Height: 1730 mm Thickness - As per standard, 1.2 mm per sheet Infill material - Resin bonded honeycomb paper core of 120 min. fire rating Frame Profile - 120 x 70 mm, thickness 1.2 mm Frame MOC - Fire rated MS Fire Rating - 120 Minutes Bearing & Hinges - SS-304,ball bearing but hinges of size: 100 x 75 x 3 mm - 08 Nos. with 5 mm machine screw SS-304 Door Closure - STD Arm 65 Kg Capacity - 02 No. Make: Hilti/ Garg/ SS or equivalent Panic Bar - Single point locking, touchbar type: DK 1000 - 02 Pc Trim Lock - External trim lock woth lever handle & lock cylinder: TMB - 02 Pc Glass - Fire rated, Clear wired glass 200 x 300 x 11 mm - 02 No. Fasterner - Hilti HUD 10 x 70 x 95 mm - 12 Nos. - Fire Straip seal Fire Straip seal 10 x 4 mm Handle - SS-304,D-type, 22 x 250 mm - 04 No. with pull push back to back set Dead Lock - Dead lock with 70 mm cylinder C EPC - 02 set Flush tower bolt - Lever action flush tower bolt with 300 mm rode Sign board - Emergency Exit sign board - 01 No. Colour of door - Red/ Baige / Grey as finalised by STL Label Details : a) Name of the manufacturer, b) Type of fire door, c) Fire rating classification, d) Serial number of the door, e) Year of manufacture, and f) Certificate reference number. Miscellaneous : Door shall be tested and certified by any approved laboratory, the label shall specify the name of the agency and the certificate number Warranty : 5 year post installation except physical damage Certification & Test : According to IS: 3614, Report to be submitted as per Annex C of IS: 3614 alongwith Fire door test report` | No. | [22 empty] | 6 | 28000 | 168000 | bar: A; D
168000
[27 empty] | GST | 30240
[27 empty] | Total | 198240

## 1.4-Approved Makes
LIST OF APPROVED MAKE
Sr. No | Specification | Make Type
1 | G.I Pipe | Tata/ Zenith/ Jindal
2 | G.I. Fitting | Zoloto/ Unik/ Safe & Secure
3 | Branch Pipe | Greetech / Superex /safegaurd /Tulsi
4 | Hydrant Valve | Arihant /Grap, Newage, Hiren / /Bhogilal (14 SWG sheet with powder coated )
5 | Water Cum Foam Monitor | Newage/ Bhogilal/ KV Fire / Armour
6 | Hose reel Drum | Arihant/Agg/Grap/ Newage, Hiren / /Bhogilal
7 | RRL Hose Pipe | Tulsi/ Riya / Arihant
8 | NRV | Kartar/Normex/Leader/ Advance/ Kirloskar/IVC/ Forbes/ M/s. Kamala Valves Manufacturing Concern.
9 | CP GM Ball Valve | Zoloto / RB / Leader / Sant
10 | Butterfly Valve/Check valve | L&T/ Audoco/ Zoloto/ Kartar
11 | Double Flange Sluice valve | L&T/ Audoco/ Zoloto/ Kartar/ Sant
12 | Air Release Valve | L&T/ Audoco/ Zoloto/ Kartar/ Sant
13 | Pressure Gauge | H. Guru / Fie-big / Brc
14 | Pressure switch | Indfoss / Danfoss / Switzer
15 | Expansion Blow Valve | Neeta Enterprises / Safex / Cease Fire / Minimax
16 | Y Stainer | Hawa / Leader / Zoloto
17 | Hose Box FRP | Vilas Eng / Newage / Tulsi
18 | Cables / wire | Finolex / RRK Cable/ Havells
19 | Paint | Asian/ Jenson/Nicholson/ Opus
20 | Wrapping Coating | Pypecoat / IWL / Coaltek Rustech
21 | Fire Service Main Pump | Kirloskar / Maxflow /Platt/Texmo / Lubi Waterman
22 | Jockey Pump | Kirloskar / Maxflow /Platt / Lubi Waterman
23 | Booster Pump | Kirloskar / Maxflow /Platt/ Lubi Waterman
24 | Diesel Engine | Kirloskar / Maxflow /Platt/ Lubi Waterman
25 | Foot valve | Normex / C& R / Leader
26 | Ceiling Mounted Automatic Fire Extinguishers / Auto Fire Ball | Brandsdady / Minimax / Armour
27 | Sprinklers | HD / Viking / Fire Shield/ Honeywell
28 | Cables / wire | Finolex/ RRK Cable/ Polycab/Havells
29 | PVC Copper wires FR/FRLS Grade | Finolex/ RRK Cable/ Polycab/Havells
30 | LT PVC / XLPE / FRLS Armoured Aluminium / Copper Cables | Finolex/ RRK Cable/ Polycab/Havells
31 | Fire Alarm Panel | Hochiki/ Bosch/ Esser/ Apollo/ Ravel/Aties
32 | Modules / MCP | Hochiki/ Bosch/ Esser/ Apollo/ Ravel/Aties
33 | Detectors | Hochiki/ Bosch/ Esser/ Apollo/ Ravel/Aties
34 | Hooter with Strobe | Hochiki/ Bosch/ Esser/ Apollo/ Ravel/Aties
35 | Response Indicator | MC Engineering / Maths / Mehta & Associates / STD or as approved by Santhan, PMC, Engineer – in- charge.
36 | Detector Testing Kit | Detector Testor Testifier or Equivalent
37 | Public Address System | TOA/ Aties/ TSG/ Honeywell
38 | PVC Conduit | ISI Make as approved by Santhan, PMC, Engineer – in- charge.

## 1.4-Budget
FHS | 7856186.3 | 7707911.04
FSS | 6324267.289 | 5986273.6586
FAS | 4962084.08 | 4438562.92
PP | 198240 | 198240
Total | 19340777.669 | 18330987.6186
Round
Target | 19426927 | 19426927
Diff | -86149.331 | 1095939.3814
-14358.2218